## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 05:49
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF350M443N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.41244 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 7.2448 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: |  |  |  |  | 10 |  | 135 | 140 |  |  | m3/hr
Pressure: | [6 empty] | 8 | 10 |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 40 |  |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: |  |  |  |  | 890 |  | 890 | 895 |  |  | kg/m3
Viscosity: |  |  |  |  | 25.93 |  | 35 | 40.69 |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 40 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
140 |  | 0.1 |  |  | 0.4379 |  |  |  | 7.5131 |  | 12322.4044
135 |  | 0.1 |  |  | 0.41244 |  |  |  | 7.2448 |  | 11882.3185
114 |  | 0.1 |  |  | 0.31308 |  |  |  | 6.1178 |  | 10033.9579
101 |  | 0.1 |  |  | 0.25754 |  |  |  | 5.4202 |  | 8889.7346
88 |  | 0.1 |  |  | 0.20642 |  |  |  | 4.7225 |  | 7745.5113
75 |  | 0.1 |  |  | 0.15968 |  |  |  | 4.0249 |  | 6601.2881
62 |  | 0.1 |  |  | 0.11741 |  |  |  | 3.3272 |  | 5457.0648
49 |  | 0.1 |  |  | 0.079894 |  |  |  | 2.6296 |  | 4312.8415
36 |  | 0.1 |  |  | 0.047764 |  |  |  | 1.932 |  | 3168.6183
23 |  | 0.1 |  |  | 0.022179 |  |  |  | 1.2343 |  | 2024.395
10 |  | 0.1529 |  |  | 0.005233 |  |  |  | 0.53665 |  | 880.1717
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT16 - Poeni2