## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-29 21:30
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF300M372N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.22275 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 4.8668 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: | [6 empty] | 55 | 60 |  |  | m3/hr
Pressure: | [6 empty] | 2 | 6 |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 16 |  |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: | [6 empty] | 830 |  |  |  | kg/m3
Viscosity: | [6 empty] | 50 |  |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 16 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
60 |  | 0.1 |  |  | 0.25634 |  |  |  | 5.3093 |  | 4746.9262
55 |  | 0.1 |  |  | 0.22275 |  |  |  | 4.8668 |  | 4351.3491
48.6554 |  | 0.1 |  |  | 0.18385 |  |  |  | 4.3054 |  | 3849.395
42.9831 |  | 0.1 |  |  | 0.1525 |  |  |  | 3.8035 |  | 3400.6293
37.3108 |  | 0.1 |  |  | 0.12419 |  |  |  | 3.3016 |  | 2951.8637
31.6386 |  | 0.1 |  |  | 0.0986 |  |  |  | 2.7996 |  | 2503.0981
25.9663 |  | 0.1 |  |  | 0.075334 |  |  |  | 2.2977 |  | 2054.3324
20.294 |  | 0.1 |  |  | 0.053953 |  |  |  | 1.7958 |  | 1605.5668
14.6217 |  | 0.1 |  |  | 0.034214 |  |  |  | 1.2938 |  | 1156.8011
8.9494 |  | 0.1 |  |  | 0.016674 |  |  |  | 0.79192 |  | 708.0355
3.2771 |  | 0.25014 |  |  | 0.004345 |  |  |  | 0.28998 |  | 259.2699
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT1