## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 09:44
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF400M443N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.16009
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.009695 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 0.99485 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: |  |  |  |  | 1 |  | 30 | 250 |  |  | m3/hr
Pressure: | [6 empty] | 2 | 3 |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 20 | 35 |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: |  |  |  |  | 800 |  | 850 | 930 |  |  | kg/m3
Viscosity: |  |  |  |  | 50 |  | 10 | 10 |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 35 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
250 |  | 0.1 |  |  | 0.45382 |  |  |  | 8.2904 |  | 60540.5086
225.1 |  | 0.1 |  |  | 0.37204 |  |  |  | 7.4647 |  | 54510.6739
200.2 |  | 0.1 |  |  | 0.29788 |  |  |  | 6.6389 |  | 48480.8393
175.3 |  | 0.1 |  |  | 0.23148 |  |  |  | 5.8132 |  | 42451.0046
150.4 |  | 0.1 |  |  | 0.173 |  |  |  | 4.9875 |  | 36421.17
125.5 |  | 0.1 |  |  | 0.12261 |  |  |  | 4.1618 |  | 30391.3353
100.6 |  | 0.1 |  |  | 0.080505 |  |  |  | 3.336 |  | 24361.5007
75.7 |  | 0.1 |  |  | 0.046958 |  |  |  | 2.5103 |  | 18331.666
50.8 |  | 0.1 |  |  | 0.022521 |  |  |  | 1.6846 |  | 12301.8314
30 |  | 0.16009 |  |  | 0.009695 |  |  |  | 0.99485 |  | 7264.861
1 |  | 4.8027 |  |  | 6.6e-05 |  |  |  | 0.033162 |  | 242.162
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT Brazi2