## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 09:45
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF200M369N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.18223 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 3.1833 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: |  |  |  |  | 1 |  | 13 | 20 |  |  | m3/hr
Pressure: | [6 empty] | 8 |  |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 48 | 50 |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: |  |  |  |  | 840 |  | 850 | 855 |  |  | kg/m3
Viscosity: | [6 empty] | 13 |  |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN50 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 50 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
20 |  | 0.1 |  |  | 0.39552 |  |  |  | 4.8974 |  | 10123.8309
18.1 |  | 0.1 |  |  | 0.33089 |  |  |  | 4.4322 |  | 9162.0669
16.2 |  | 0.1 |  |  | 0.27115 |  |  |  | 3.9669 |  | 8200.303
14.3 |  | 0.1 |  |  | 0.21652 |  |  |  | 3.5017 |  | 7238.5391
13 |  | 0.1 |  |  | 0.18223 |  |  |  | 3.1833 |  | 6580.4901
10.5 |  | 0.1 |  |  | 0.12368 |  |  |  | 2.5712 |  | 5315.0112
8.6 |  | 0.1 |  |  | 0.086114 |  |  |  | 2.1059 |  | 4353.2473
6.7 |  | 0.1 |  |  | 0.055032 |  |  |  | 1.6406 |  | 3391.4833
4.8 |  | 0.1 |  |  | 0.031008 |  |  |  | 1.1754 |  | 2429.7194
2.9 |  | 0.1 |  |  | 0.014235 |  |  |  | 0.71013 |  | 1467.9555
1 |  | 0.25615 |  |  | 0.003225 |  |  |  | 0.24487 |  | 506.1915
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT12 - Aricesti