## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 09:46
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF300M372N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.36533 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 6.1942 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: | [6 empty] | 70 | 80 |  |  | m3/hr
Pressure: | [6 empty] | 20 |  |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 13 |  |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: | [6 empty] | 860 |  |  |  | kg/m3
Viscosity: | [6 empty] | 60 |  |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 13 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
80 |  | 0.1 |  |  | 0.45535 |  |  |  | 7.079 |  | 5274.3625
70 |  | 0.1 |  |  | 0.36533 |  |  |  | 6.1942 |  | 4615.0672
64.6326 |  | 0.1 |  |  | 0.32147 |  |  |  | 5.7192 |  | 4261.1943
56.9488 |  | 0.1 |  |  | 0.26404 |  |  |  | 5.0393 |  | 3754.6101
49.2651 |  | 0.1 |  |  | 0.21268 |  |  |  | 4.3594 |  | 3248.026
41.5814 |  | 0.1 |  |  | 0.16692 |  |  |  | 3.6795 |  | 2741.4419
33.8977 |  | 0.1 |  |  | 0.12599 |  |  |  | 2.9995 |  | 2234.8578
26.214 |  | 0.1 |  |  | 0.088976 |  |  |  | 2.3196 |  | 1728.2737
18.5302 |  | 0.1 |  |  | 0.055149 |  |  |  | 1.6397 |  | 1221.6895
10.8465 |  | 0.1 |  |  | 0.02524 |  |  |  | 0.95979 |  | 715.1054
3.1628 |  | 0.25014 |  |  | 0.004975 |  |  |  | 0.27987 |  | 208.5213
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT2 - Moreni