## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 09:47
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF300M372N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.070153 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 2.7431 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: |  |  |  |  | 1 |  | 31 | 40 |  |  | m3/hr
Pressure: | [6 empty] | 10 |  |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 60 |  |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: |  |  |  |  | 820 |  | 825 | 829 |  |  | kg/m3
Viscosity: | [6 empty] | 28 |  |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 60 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
40 |  | 0.1 |  |  | 0.10689 |  |  |  | 3.5395 |  | 5651.1027
36.1 |  | 0.1 |  |  | 0.08994 |  |  |  | 3.1944 |  | 5100.1202
31 |  | 0.1 |  |  | 0.070153 |  |  |  | 2.7431 |  | 4379.6046
28.3 |  | 0.1 |  |  | 0.060767 |  |  |  | 2.5042 |  | 3998.1551
24.4 |  | 0.1 |  |  | 0.048504 |  |  |  | 2.1591 |  | 3447.1726
20.5 |  | 0.1 |  |  | 0.037677 |  |  |  | 1.814 |  | 2896.1901
16.6 |  | 0.1 |  |  | 0.028108 |  |  |  | 1.4689 |  | 2345.2076
12.7 |  | 0.1 |  |  | 0.019556 |  |  |  | 1.1238 |  | 1794.2251
8.8 |  | 0.1 |  |  | 0.011809 |  |  |  | 0.7787 |  | 1243.2426
4.9 |  | 0.16831 |  |  | 0.00503 |  |  |  | 0.43359 |  | 692.2601
1 |  | 0.82471 |  |  | 0.000659 |  |  |  | 0.088488 |  | 141.2776
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT5 - Bucsani