## Sheet1 (2)
Micro Motion Calculation Summary
Date: | [5 empty] | 2026-07-31 09:47
Company:
Project Name: | [5 empty] | 4000-BUS-16-0011894
Service:
Sensor Model #: | [5 empty] | CMF300M372N2FZEZZZMCIC
Sensor Tag(s):
Transmitter Model #: | [5 empty] | 2700R12ACFEZWZPK
Transmitter Tag(s):
Wetted Material: | [5 empty] | 316L stainless steel
Fluid: | [5 empty] | Crude oil
Fluid State: | [5 empty] | Liquid
Mass Flow Accuracy at Operating. Flow (+/- % of Rate): | [5 empty] | 0.1
Density Accuracy at all Rates ( +/- ): | [5 empty] | 0.5 | kg/m3
Pressure Drop at Operating Flow: | [5 empty] | 0.24859 | bar
Sensor Minimum Pressure at operating conditions: | [6 empty] | bar-g
Velocity at Operating Flow: | [5 empty] | 4.9553 | m/sec
[5 empty] | Min |  | Operating* | Max |  | Design | Units
Flow Rate: |  |  |  |  | 1 |  | 56 | 60 |  |  | m3/hr
Pressure: | [6 empty] | 17 | 20 |  |  | bar-g
Process Fluid Temperature: | [6 empty] | 47 |  |  |  | C
Ambient Temperature: | [6 empty] | 15 |  |  |  | C
Density: |  |  |  |  | 890 |  | 900 | 905 |  |  | kg/m3
Viscosity: |  |  |  |  | 30 |  | 50 | 60 |  |  | centistokes
| Base Reference Temperature: |  |  | F | [5 empty] | Density:
Gas only | Base Reference Pressure: |  |  | psia
| Base Reference Density: |  |  | kg/m3
Process Connection: | [5 empty] | DN100 PN40 EN 1092-1 F316/F316L Weld neck flange Form B1
Process Connection Pressure Rating: | [5 empty] | 39.9896 | bar-g
@ Temperature: | [5 empty] | 47 | C
Flow Rate | m3/hr |  | Mass Flow Accuracy +/- % of | Rate |  | Pressure Drop* | bar |  | Velocity* | m/sec | Re
60 |  | 0.1 |  |  | 0.27796 |  |  |  | 5.3093 |  | 4746.9262
56 |  | 0.1 |  |  | 0.24859 |  |  |  | 4.9553 |  | 4430.4645
48.2 |  | 0.1 |  |  | 0.1965 |  |  |  | 4.2651 |  | 3813.3641
42.3 |  | 0.1 |  |  | 0.16149 |  |  |  | 3.743 |  | 3346.583
36.4 |  | 0.1 |  |  | 0.13001 |  |  |  | 3.221 |  | 2879.8019
30.5 |  | 0.1 |  |  | 0.10167 |  |  |  | 2.6989 |  | 2413.0208
24.6 |  | 0.1 |  |  | 0.075933 |  |  |  | 2.1768 |  | 1946.2398
18.7 |  | 0.1 |  |  | 0.052309 |  |  |  | 1.6547 |  | 1479.4587
12.8 |  | 0.1 |  |  | 0.030647 |  |  |  | 1.1326 |  | 1012.6776
6.9 |  | 0.10956 |  |  | 0.012487 |  |  |  | 0.61057 |  | 545.8965
1 |  | 0.75599 |  |  | 0.001204 |  |  |  | 0.088488 |  | 79.1154
*All pressure drop and velocity results are based on the process conditions (except flow rate) that are entered in the Operating column.
Notes:
Prepared by: |  |  |  |  | Project ID: |  |  | 4000-BUS-16-0011894 : 1026270
Instrument Toolkit |  | Version: 3.0 (Build201A) |  |  | Application: |  |  | FT6 - Ochiuri