## Front Cover
DIAGRAMA CAUZĂ - EFECT STAȚIA DE POMPARE SLOBOZIA
01 | 05.2022 | Emis pentru construire | DAN M. | NAN J.C. | STAN C. |  | NAN J.C.
00 | 06.2021 | Emis pentru comentarii | DAN M. | NAN J.C. | STAN C. |  | NAN J.C.
REV | DATA | DESCRIERE | ÎNTOCMIT | VERIFICAT | ȘEF PROIECT |  | APROBAT
ORIGINATOR
NUME PROIECT:
MODERNIZAREA STAȚIEI DE POMPARE A ȚIȚEIULUI SLOBOZIA JUDEȚUL PRAHOVA
NUMAR PROIECT:
S.C. CONPET S.A. |  | PR1193/2019
|  | FAZA PROIECT: |  |  |  | REVISION
|  | PT+DE |  |  |  | 01
|  | NUMAR DOCUMENT: |  |  |  | SHEET
S.C. TEAM OIL S.R.L |  | PR1193-PS03-01 |  |  |  | 1 | OF | 2

## C&E
S.C.CONPET S.A. |  | S.C. TEAM OIL S.R.L | MODERNIZAREA STAȚIEI DE POMPARE A ȚIȚEIULUI SLOBOZIA JUDEȚUL PRAHOVA |  | DIAGRAMA CAUZĂ - EFECT STAȚIA DE POMPARE SLOBOZIA | [6 empty] | EFECT | ACȚIUNE îNDEPLINITĂ | OPRIRE URGENȚĂ P-001 | PORNIRE URGENȚĂ P-002 | OPRIRE URGENȚĂ P-002
LEGENDĂ: |  |  |  |  | NOTE:
SOR = Start-Up Override
X | ACȚIUNE DE PROTEJARE
' | INDICĂ INTRĂRI CARE TREBUIE SĂ FIE TOATE PREZENTE
| ÎN MOD SIMULTAN PENTRU A FI GENERAT UN SEMNAL DE IEȘIRE | [11 empty] | SEMNAL | HZS-001 | HZS-001 | HZS-001
Ø | 1 DIN 2
f | 2 DIN 3
T | INDICĂ O TEMPORIZARE ÎNAINTE CA ACȚIUNEA SĂ AIBĂ LOC | [11 empty] | LISTĂ INTRĂRI / IEȘIRI | PR1193-IN002 | PR1193-IN002 | PR1193-IN002
¤ | INDICĂ FAPTUL CĂ EXECUȚIA ESTE INHIBATĂ PÂNĂ CÂND
ROBINETELE DE ÎNCHIDERE ASOCIATE AU CONFIRMAREA CĂ SUNT ÎNCHISE
R | ACȚIUNEA DE RESET | [11 empty] | SIL
CAUZĂ
ARIE SISTEM |  | INIȚIERE EVENIMENT (DESCRIERE) | INSTRUMENT | LOCATIE INSTRUMENT |  | LISTĂ INTRĂRI / IEȘIRI | P&ID | SIL | SOR | NOTE |  |  |  | 1 | 2 | 3
SIS |  | Lipsă debit în aspirația pompei P-001 | FALL-001 | INTRARE POMPĂ P001 |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - | X
SIS |  | Presiune înaltă in refularea pompei P-001 | PAHH-001 | IEȘIRE POMPĂ P001 |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - | X
SIS |  | Temperatură înaltă pompă P-001 | TAHH-002 | POMPA |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - | X
SIS |  | Nivel ridicat in bazinul colector | LAHH-001 | BAZIN COLECTOR |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - |  | X
SIS |  | Nivel scazut in bazinul colector | LALL-002 | BAZIN COLECTOR |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - |  |  | X
SIS |  | Presiune înaltă in refularea pompei P-002 | PAHH-002 | IEȘIRE POMPĂ P002 |  | PR1193-IN002 | PR1193-PS002 | - |  |  |  |  | - |  |  | X
NUME PROIECT: MODERNIZAREA STAȚIEI DE POMPARE A ȚIȚEIULUI SLOBOZIA JUD. PRAHOVA
NUMĂR PROIECT: PR1193 / 2019
FAZĂ PROIECT: PT+DE | [10 empty] | PAGINA | [5 empty] | 01 | 05.2022 | EMIS PENTRU CONSTRUIRE | DAN M. | NAN J.C. | NAN J.C.
[17 empty] | 00 | 06.2021 | EMIS PENTRU COMENTARII | DAN M. | NAN J.C. | NAN J.C.
NUMĂR DOCUMENT: PR1193-PS03-01 | [10 empty] | 2 DIN 2 | [5 empty] | REV. | DATA | DESCRIERE | INTOCMIT | VERIFICAT | APROBAT

## C&E Diagram 4 (hidden)
|  |  |  | S.C STRATUM ENERGY ROMANIA LLC WILMINGTON SUCURSALA BLEJOI |  | CAUSE AND EFFECT DIAGRAM | [7 empty] | EFFECT | P&ID |  | 6/18 | 4/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 6/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 10/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18 | 11/18
S.C. TEAM OIL S.R.L.
PLOIESTI
LEGEND: | [14 empty] | PERFORMED ACTION |  | Inchidere la avarie | Inchidere la avarie | ALARMA H=50bar | ALARMA L=27bar | ALARMA H=750mm,ESD01 | ALARMA L=50mm | ALARMA L=50mm | ALARMA L=100mm | INDICATOR ON/OFF 21-SDV-001 | ON/OFF | ALARMA H=100kPa | ALARMA H=10mc/h | ALARMA H=5mc/h | ALARMA H=650mm | ALARMA L=100mm | ALARMA H=35°C/PSD | ALARMA H=-26°C/PSD | ALARMA H=100kPa | ALARMA H=1630mm | ALARMA L=700mm,Inchide 310-SDV-001 | ON/OFF | ALARMA H=100kPa | ALARMA H=1630mm | ALARMA L=700mm,Inchide 310-SDV-002 | ON/OFF | ALARMA H≠0NMC/d | ALARMA H≠0NMC/d | ALARMA H=40kPa | ALARMA H=40kPa | ALARMA H=40kPa | ALARMA H=40kPa | ALARMA H=-3°C | ALARMA H=15°C | ALARMA H=60bar | ALARMA L=26.5bar | ALARMA H=-3°C/PSD | ALARMA H=60bar | ALARMA L=27bar | ALARMA H=100kPa | ALARMA L=0kPa | ALARMA H=-4°C | ALARMA L=-20°C | ALARMA H=700mm | ALARMA L=50mm/PSD
SOR = Start-Up Override
X |  | SAFEGUARDING ACTION
' |  | INDICATES INPUTS WHICH MUST ALL BE PRESENT
|  | SIMULTANEOUSLY FOR AN OUTPUT SIGNAL TO BE GENERATED | [12 empty] | TAG NUMBER |  | SDV-701 | SDV-040 | 21-PAH-001 | 21-PAL-001 | 210-LAH-001 | 210-LAL-001 | 210-LAL-002 | 210-ILAL-001 | 210-ILC-001 | 21-SDV-001 | 210-PDAH-001 | 21-FAH-002 | 21-FAH-003 | 210-LAH-001 | 210-LAL-003 | 31-TAH-001 | 31-WDPT-001 | 310-PDAH-001 | 310-LAHH-001 | 310-LAL-001 | 310-SDV-001 | 310-PDAH-002 | 310-LAHH-001 | 310-LAL-002 | 310-SDV-002 | 31-FAHH-001 | 31-FAHH-002 | 311-PDAH-001 | 311-PDAH-002 | 311-PDAH-002 | 312-PDAH-002 | 31-TAH-006 | 31-TAH-007 | 31-PAH-006 | 31-PAL-006 | 31-HDPIT-001 | 31-PAH-005 | 31-PAL-005 | 313-PDAH-001 | 313-PDAL-001 | 313-TAH-001 | 313-TAL-001 | 313-LAHH-001 | 313-LALL-001
Ø |  | 1 OUT OF 2
f |  | 2 OUT OF 3
T |  | INDICATES A TIME DELAY BEFORE THE ACTION TAKES PLACE | [12 empty] | LOGIC DIAGRAM
¤ |  | INDICATES THAT EXECUTION IS INHIBITED UNTIL ASSOCIATED
SHUTDOWN VALVES ARE CONFIRMED CLOSED
R |  | RESET ACTION | [12 empty] | SIL
CAUSE
SYSTEM AREA |  |  | INITIATING EVENT (DESCRIPTION) |  | INSTRUMENT TAG NUMBER |  | INSTRUMENT LOCATION | LOGIC DIAGRAM | P&ID | SIL | SOR's | NOTES |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44
PCS |  |  | Masurare presiune |  | 21-PT-001 |  | 210-V-001 |  | 6/18 | [5 empty] | A | bar: 1 to 32
PCS |  |  | Indicator de nivel |  | 210-LSH-001 |  | 210-V-001 |  | 6/18 | [5 empty] | B | bar: 1 to 32
PCS |  |  | Indicator de nivel |  | 210-LSL-001 |  | 210-V-001 |  | 6/18 | [5 empty] | C | bar: 1 to 32
PCS |  |  | Indicator de nivel |  | 210-LSL-002 |  | 210-V-001 |  | 6/18 | [5 empty] | D | bar: 1 to 32
PCS |  |  | Masurare concentratie-Alarma |  | 210-ILS-001 |  | 210-V-001 |  | 6/18 | [5 empty] | E | bar: 1 to 32
PCS |  |  | Masurare concentratie-Control |  | 210-ILT-001 |  | 210-V-001 |  | 6/18 | [5 empty] | F | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 21-ZIO-001 |  | 21-SDV-001 |  | 6/18 | [5 empty] | G | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 21-ZIC-001 |  | 21-SDV-001 |  | 6/18 | [5 empty] | H | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 210-PDT- 001 |  | 210-V-001 |  | 6/18 | [5 empty] | I | bar: 1 to 32
PCS |  |  | Masurare debit |  | 21-FT-002 |  | 50-PC-002-ACQ3A-CI |  | 6/18 | [5 empty] | J | bar: 1 to 32
PCS |  |  | Masurare debit |  | 21-FT-003 |  | 50-PL-001-ACQ3A-ET |  | 6/18 | [5 empty] | K | bar: 1 to 32
PCS |  |  | Masurare nivel |  | 210-LT-001 |  | 210-V-001 |  | 6/18 | [5 empty] | L | bar: 1 to 32
PCS |  |  | Masurare temperatura |  | 31-TT-001 |  | 150-GN-001-ACQ3A-CI |  | 10/18 | [5 empty] | M | bar: 1 to 32
PCS |  |  | Alarma-Punct de roua |  | 31-WDPT-001 |  | 310-F-001A |  | 10/18 | [5 empty] | N | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 310-PDT-001 |  | 310-F-001A |  | 10/18 | [5 empty] | O | bar: 1 to 32
PCS |  |  | Indicator nivel |  | 310-LSH-001 |  | 310-F-001A |  | 10/18 | [5 empty] | P | bar: 1 to 32
PCS |  |  | Indicator nivel |  | 310-LSL-001 |  | 310-F-001A |  | 10/18 | [5 empty] | Q | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 310-ZIO-001 |  | 310-SDV-001 |  | 10/18 | [5 empty] | R | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 310-ZIC-001 |  | 310-SDV-001 |  | 10/18 | [5 empty] | S | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 310-PDT-002 |  | 310-F-001B |  | 10/18 | [5 empty] | T | bar: 1 to 32
PCS |  |  | Indicator nivel |  | 310-LSH-002 |  | 310-F-001B |  | 10/18 | [5 empty] | U | bar: 1 to 32
PCS |  |  | Indicator nivel |  | 310-LSL-002 |  | 310-F-001B |  | 10/18 | [5 empty] | V | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 310-ZIO-002 |  | 310-SDV-002 |  | 10/18 | [5 empty] | W | bar: 1 to 32
PCS |  |  | Indicator pozitie |  | 310-ZIC-002 |  | 310-SDV-002 |  | 10/18 | [5 empty] | X | bar: 1 to 32
PCS |  |  | Senzor curgere |  | 31-FS-001 |  | 100-AV-002-ACQ3A-VP |  | 10/18 | [5 empty] | Y | bar: 1 to 32
PCS |  |  | Senzor curgere |  | 31-FS-002 |  | 50-AV-006-ACQ3A-VP |  | 10/18 | [5 empty] | Z | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 311-PDT-001 |  | 311-E-001 |  | 11/18 | [5 empty] | AA | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 311-PDT-002 |  | 311-E-001 |  | 11/18 | [5 empty] | AB | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 312-PDT-001 |  | 312-E-001 |  | 11/18 | [5 empty] | AC | bar: 1 to 32
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 312-PDT-002 |  | 312-E-001 |  | 11/18 | [5 empty] | AD | bar: 1 to 32
PCS |  |  | Masurare temperatura |  | 31-TT-006 |  | 150-GN-009-ACQ3A-CI |  | 11/18 | [5 empty] | AE | bar: 1 to 32
PCS |  |  | Masurare temperatura |  | 31-TT-007 |  | 150-GN-003-ACQ3A-CI |  | 11/18 | [5 empty] | AF | bar: 1 to 33
PCS |  |  | Masurare presiune |  | 31-PT-006 |  | 150-GN-003-ACQ3A-CI |  | 11/18 | [5 empty] | AG | bar: 1 to 35
PCS |  |  | Alarma HC punct de roua |  | 31-HDPT-001 |  | 150-GN-003-ACQ3A-CI |  | 11/18 | [5 empty] | AH | bar: 1 to 36
PCS |  |  | Masurare presiune |  | 31-PT-005 |  | 150-GN-009-ACQ3A-CI |  | 11/18 | [5 empty] | AI | bar: 1 to 38
PCS |  |  | Masurare presiune diferentiala-Alarma |  | 313-PDT-001 |  | 313-V-001 |  | 11/18 | [5 empty] | AJ | bar: 1 to 40
PCS |  |  | Masurare temperatura-Alarma |  | 313-TT-001 |  | 313-V-001 |  | 11/18 | [5 empty] | AK | bar: 1 to 42
PCS |  |  | Indicator nivel |  | 313-LSHH-001 |  | 313-V-001 |  | 11/18 | [5 empty] | AL | bar: 1 to 35; 37 to 43
PCS |  |  | Indicator nivel |  | 313-LSLL-001 |  | 313-V-001 |  | 11/18 | [5 empty] | AM | bar: 1 to 44
PROJECT NAME: FACILITATI DE SUPRAFATA PENTRU EXPLOATAREA DE GAZE P1 PODURI
PROJECT NUMBER: 955/2015
[18 empty] | 2 |  | 5.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [13 empty] | Popa A. | [7 empty] | NAN J. | [7 empty] | TRUSU M.
PROJECT PHASE: DE | [12 empty] | SHEET |  |  |  | 2: 1; 4: 2.2014; 8: EMIS PENTRU CONSTRUIRE; 22: Popa A.; 30: NAN J.; 38: TRUSU M.
[18 empty] | 0 |  | 01.01.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [13 empty] | Popa A. | [7 empty] | NAN J. | [7 empty] | TRUSU M.
DOCUMENT NUMBER: PR955-IN019-1_C&E DIAGRAM | [12 empty] | 4 | OF |  | 7 | 2: REV; 4: DATE; 8: DESCRIPTION; 22: PREPARED; 30: CHECKED; 38: APPROVED
ORIGINATOR

## C&E Diagram 5 (hidden)
|  |  |  | S.C STRATUM ENERGY ROMANIA LLC WILMINGTON SUCURSALA BLEJOI |  | CAUSE AND EFFECT DIAGRAM | [8 empty] | EFFECT | P&ID |  | 11/18 | 11/18 | 11/18 | 11/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 |  | 12/18 | 12/18 | 12/18 | 12/18 | 12/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18 | 13/18
S.C. TEAM OIL S.R.L.
PLOIESTI
LEGEND: | [7 empty] | NOTES: | [7 empty] | PERFORMED ACTION |  | ESD-01/PSD | ON/OFF | ALARMA H=600mm | ALARMA L=100mm | ALARMA H=2mc/h | ALARMA H=62bar | ALARMA L=35bar | ALARMA H=75°C | ALARMA L=45°C | PA≥5bar | H=5barg/PSD | ON/OFF | ALARMA H=750mm | ALARMA L=50mm | ALARMA L=50mm+OFF 40-SDV-006 | ON/OFF | ON/OFF 40-SDV-006 | ALARMA L=300mm | ALARMA H=650mm | ALARMA L=100mm | PSD | ON/OFF | ALARMA H=1.8barg | ALARMA L=1.2barg | ALARMA H=40°C | ALARMA H=10°C | ALARMA H=20kPa | ALARMA H=20kPa | ALARMA H=20kPa | ALARMA H=20kPa | ALARMA H=61bar | ALARMA L=26.5bar | ALARMA H=5barg | ON/OFF | ON/OFF-PSD | ON/OFF | ALARMA H=5barg | ON/OFF | PSD | ON/OFF | PSD | ON/OFF
SOR = Start-Up Override
X |  | SAFEGUARDING ACTION
' |  | INDICATES INPUTS WHICH MUST ALL BE PRESENT
|  | SIMULTANEOUSLY FOR AN OUTPUT SIGNAL TO BE GENERATED | [13 empty] | TAG NUMBER |  | 31-HS-001 | 31-SDV-001 | 31-LAH-001 | 31-LAL-001 | 31-FAH-001 | 40-PAH-005 | 40-PAL-005 | 40-TAH-001(005) | 40-TAL-001(005) | 400-HS-001 | 40-HS-001 | 40-SDV-001 | 401-LAH-001 | 401-LAL-001 | 401-LAL-001 | 40-SDV-006 | 40-ILC-001 | 401-ILAL-001 | 401-LAH-001 | 401-LAL-001 | 40-HS-002 | 40-SDV-001 | 40-PAH-010 | 40-PAL-001 | 40-TAH-012 | 40-TAH-010 | 402-PDAH-002 | 403-PDT-002 | 402-PDAH-001 | 403-PDAH-001 | 40-PAH-011 | 40-PAL-011 | 40-PAH-003 | 40-SDV-003 | 40-SDV-005 | 40-SDV-005 | 40-PAH-002 | 40-SDV-004 | 40-HS-004 | 40-SDV-004 | 40-HS-003 | 40-SDV-003
Ø |  | 1 OUT OF 2
f |  | 2 OUT OF 3
T |  | INDICATES A TIME DELAY BEFORE THE ACTION TAKES PLACE | [13 empty] | LOGIC DIAGRAM
¤ |  | INDICATES THAT EXECUTION IS INHIBITED UNTIL ASSOCIATED
SHUTDOWN VALVES ARE CONFIRMED CLOSED
R |  | RESET ACTION | [13 empty] | SIL
CAUSE
SYSTEM AREA |  |  | INITIATING EVENT (DESCRIPTION) |  | INSTRUMENT TAG NUMBER |  | INSTRUMENT LOCATION |  | LOGIC DIAGRAM | P&ID | SIL | SOR's | NOTES |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42
PCS |  |  | 31-SDV-001 ON/OFF |  | 31-HS-001 |  | 31-SDV-001 |  |  | 11/18 | [5 empty] | A | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 31-ZIO-001 |  | 313-V-001 |  |  | 11/18 | [5 empty] | B | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 31-ZIC-001 |  | 313-V-001 |  |  | 11/18 | [5 empty] | C | bar: 1 to 35
PCS |  |  | Masurare nivel |  | 313-LT-001 |  | 313-V-001 |  |  | 11/18 | [5 empty] | D | bar: 1 to 35
PCS |  |  | Masurare temperatura |  | 31-TT-009 |  | 50-PCS-001-ACQ3A-CI |  |  | 11/18 | [5 empty] | E | bar: 5 to 35
PCS |  |  | Masurare debit |  | 31-FT-001 |  | 50-PCS-001-ACQ3A-CI |  |  | 11/18 | [5 empty] | F | bar: 1 to 35
PCS |  |  | Masurare presiune |  | 40-PT-005 |  | 80-PC-005-ACQ3A-CI |  |  | 12/18 | [5 empty] | G | bar: 1 to 35
PCS |  |  | Masurare temperatura |  | 40-TT-005 |  | 80-PC-006-ACQ3A-CI |  |  | 12/18 | [5 empty] | H | bar: 1 to 35
PCS |  |  | 40-E-001 ON/OFF Control |  | 40-PC-001 |  | 80-PC-006-ACQ3A-CI |  |  | 12/18 | [5 empty] | I | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-HS-001 |  | 400-E-001 |  |  | 12/18 | [5 empty] | J | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIO-001 |  | 40-SDV-006 |  |  | 12/18 | [5 empty] | K | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIC-001 |  | 40-SDV-006 |  |  | 12/18 | [5 empty] | L | bar: 1 to 35
PCS |  |  | Indicator nivel |  | 401-LSH-001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | M | bar: 1 to 35
PCS |  |  | Indicator nivel |  | 401-LSL-001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | N | bar: 1 to 35
PCS |  |  | Indicator nivel |  | 401-LSL-002 |  | 401-V-001 |  |  | 12/18 | [5 empty] | O | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIO-006 |  | 40-SDV-006 |  |  | 12/18 | [5 empty] | P | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIC-006 |  | 40-SDV-006 |  |  | 12/18 | [5 empty] | Q | bar: 1 to 35
PCS |  |  | Masurare concentratie/Control |  | 401-ILC-001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | R | bar: 1 to 35
PCS |  |  | Masurare conventratie/Alarma |  | 401-ILS-001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | S | bar: 1 to 35
PCS |  |  | Masurare nivel |  | 401-LT-001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | T | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-HS-002 |  | PCS |  |  | 12/18 | [5 empty] | U | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIO-002 |  | 40-SDV-002 |  |  | 12/18 | [5 empty] | V | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIC-002 |  | 40-SDV-002 |  |  | 12/18 | [5 empty] | W | bar: 1 to 35
PCS |  |  | Masurare presiune |  | 40-PT-010 |  | 150-GN-007-ACQ3A-CI |  |  | 13/18 | [5 empty] | X | bar: 1 to 35
PCS |  |  | Masurare temperatura |  | 40-TT-012 |  | 150-GN-007-ACQ3A-CI |  |  | 13/18 | [5 empty] | Y | bar: 1 to 35
PCS |  |  | Masurare temperatura |  | 40-TT-010 |  | 150-GN-005-ACQ3A-CI |  |  | 13/18 | [5 empty] | Z | bar: 1 to 35
PCS |  |  | Masurare presiune diferentiala |  | 402-PDT- 002 |  | 402-E-001 |  |  | 13/18 | [5 empty] | AA | bar: 1 to 35
PCS |  |  | Masurare presiune diferentiala |  | 403-PDT- 002 |  | 403-E-001 |  |  | 13/18 | [5 empty] | AB | bar: 1 to 35
PCS |  |  | Masurare presiune diferentiala |  | 402-PDT- 001 |  | 402-E-001 |  |  | 13/18 | [5 empty] | AC | bar: 1 to 35
PCS |  |  | Masurare presiune diferentiala |  | 403-PDT-001 |  | 402-E-001 |  |  | 13/18 | [5 empty] | AD | bar: 1 to 35
PCS |  |  | Masurare presiune |  | 40-PT-011 |  | 50-PC-014-ECQ3A-CI |  |  | 13/18 | [5 empty] | AE | bar: 1 to 35
PCS |  |  | Indicator presiune |  | 40-PS-003 |  | 50-PC-016-ACQ3A-CI |  |  | 13/18 | [5 empty] | AF | bar: 1 to 35
PCS |  |  | 40-SDV-005 ON/OFF |  | 40-PC-003 |  | PCS |  |  | 13/18 | [5 empty] | AG | bar: 1 to 35
PCS |  |  | 40-SDV-004 ON/OFF Control |  | 40-HS-005 |  | 40-SDV-005 |  |  | 13/18 | [5 empty] | AH | bar: 1 to 35
PCS |  |  | Indicator pozitie |  | 40-ZIO-005 |  | 40-SDV-005 |  |  | 13/18 | [5 empty] | AI | bar: 1 to 36
PCS |  |  | Indicator pozitie |  | 40-ZIC-005 |  | 40-SDV-005 |  |  | 13/18 | [5 empty] | AJ | bar: 1 to 36
PCS |  |  | Indicator pozitie |  | 40-PS-002 |  | 50-PC-011-ACQ3A-CI |  |  | 13/18 | [5 empty] | AK | bar: 1 to 37
PCS |  |  | 40-SDV-0013 ON/OFF |  | 40-PC-002 |  | PCS |  |  | 13/18 | [5 empty] | AL | bar: 1 to 38
PCS |  |  | 40-SDV-005 ON/OFF |  | 40-HS-004 |  | PCS |  |  | 13/18 | [5 empty] | AM | bar: 1 to 39
PCS |  |  | Indicator pozitie |  | 40-ZIO-004 |  | 40-SDV-004 |  |  | 13/18 | [5 empty] | AN | bar: 1 to 35; 37 to 40
PCS |  |  | Indicator pozitie |  | 40-ZIC-004 |  | 40-SDV-004 |  |  | 13/18 | [5 empty] | AO | bar: 1 to 35; 37 to 40
PCS |  |  | 40-SDV-003 ON/OFF |  | 40-HS-003 |  | PCS |  |  | 13/18 | [5 empty] | AP | bar: 1 to 38; 40 to 41
PCS |  |  | Indicator pozitie |  | 40-ZIO-003 |  | 40-SDV-003 |  |  | 13/18 | [5 empty] | AQ | bar: 1 to 35; 37 to 39; 41 to 42
PCS |  |  | Indicator pozitie |  | 40-ZIC-003 |  | 40-SDV-003 |  |  | 13/18 | [5 empty] | AR | bar: 1 to 35; 37 to 39; 41 to 42
PROJECT NAME: FACILITATI DE SUPRAFATA PENTRU EXPLOATAREA DE GAZE P1 PODURI
PROJECT NUMBER: 856/2012
[19 empty] | 2 |  | 05.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [13 empty] | NAN J. |  |  | Popa A. | [7 empty] | NAN J. | [7 empty] | TRUSU M.
PROJECT PHASE: DE | [13 empty] | SHEET |  |  |  | 2: 1; 4: 2.2014; 8: EMIS PENTRU CONSTRUIRE; 22: NAN J.; 25: Popa A.; 33: NAN J.; 41: TRUSU M.
[19 empty] | 0 |  | 01.01.204 |  |  |  | EMIS PENTRU CONSTRUIRE | [16 empty] | Popa A. | [7 empty] | NAN J. | [7 empty] | TRUSU M.
DOCUMENT NUMBER: PR856-IN019-1_C&E DIAGRAM | [13 empty] | 5 | OF |  | 7 | 2: REV; 4: DATE; 8: DESCRIPTION; 25: PREPARED; 33: CHECKED; 41: APPROVED

## C&E Diagram 6 (hidden)
|  |  |  | S.C STRATUM ENERGY ROMANIA LLC WILMINGTON SUCURSALA BLEJOI |  | CAUSE AND EFFECT DIAGRAM | [8 empty] | EFFECT | P&ID |  |  |  |  | 13/18 | 12/18 | 12/18 | 12/18 | 7/18 | 7/18 | 7/18 | 7/18 | 9/18 | 9/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 7/18 | 8/18 | 8/18 | 8/18 | 8/18 | 8/18 | 8/18 | 8/18 | 8/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18
S.C. TEAM OIL S.R.L.
PLOIESTI
LEGEND: | [7 empty] | NOTES: | [7 empty] | PERFORMED ACTION |  | Inchidere la avarie | Inchidere la avarie | Inchidere la avarie | ALARMA H=6.5mc/h | PSD | ALARMA H=100kPa | ALARMA H=5barg | ALARMA H=100°C | ALARMA H=100°C | ALARMA H=60bar | ALARMA H=100°C | ALARMA H=0.5kPa | ALARMA H=1.0kPa | ALARMA H=60°C | HH=45°C,ESD01 | LL=25°C,ESD01 | HH=90000mc/h,ESD01 | LL=12083mc/h,ESD01 | ALARMA H=60bar | ALARMA L=35bar | ALARMA H=60°C | ALARMA H=525mm | ALARMA H=800mm/PSD | ON/OFF | ALARMA L=200mm/PSD | ON/OFF | ALARMA H=1000mm | PSD | PSD | ALARMA H=725mm | ALARMA L=100mm | ALARMA H=850mm | ALARMA L=200mm | ALARMA L=50mm/PSD | ALARMA H=750mm | ALARMA H=4bar | ALARMA L=3bar | ALARMA H=100kPa | ALARMA H=100kPa | ALARMA H=5bar/PSD | ALARMA HH=100°c | ALARMA H=205°c/PSD | ALARMAH=0.2bar | ALARMA L=0.1bar | ALARMA H=10mc/h | ALARMA H=25mc/h | ALARMA H=5.4bar | ALARMA L=1bar | ALARMA H=1bar | ALARMA L=0.05bar | ALARMA L=800mm/PSD
SOR = Start-Up Override
X |  | SAFEGUARDING ACTION
' |  | INDICATES INPUTS WHICH MUST ALL BE PRESENT
|  | SIMULTANEOUSLY FOR AN OUTPUT SIGNAL TO BE GENERATED | [13 empty] | TAG NUMBER |  | SDV-060 | SDV-040 | SDV-039 | 40-FAH-001 | 40-FS-001 | 401-PDAH-001 | 40-PAH-004 | 300-TAH-001 | 302-TAH-001 | 300-PAH-001 | 302-PAH-001 | 309-PDAH-001 | 30-PDAH-002 | 30-TAH-02 | 30-TAHH-001 | 30-TALL-001 | 30-FAHH-001 | 30-FAL-001 | 30-PAH-001 | 30-PAL-001 | 301-TAH-002 | 301-LAHH-002 | 301-LAH-001 | 30-SDV-002 | 301-LALL-001 | 30-SDV-001 | 301-LAHH-001 | 30-HS-001 | 30-HS-002 | 301-LAH-001 | 301-LAL-001 | 305-LAH-001 | 305-LAL-001 | 305-LALL-001 | 305-LAHH-750mm | 30-PAH-002 | 30-PAL-002 | 307-PDAH-001 | 308-PDAH-001 | 309-PAHH-001 | 309-TAH-001 | 309-TAH-002 | 30-PAH-003 | 30-PAL-003 | 30-FAH-003 | 30-FAH-002 | 30-PAH-005 | 30-PAL-005 | 30-PAH-004 | 30-PAL-004 | 309-LALL-001
Ø |  | 1 OUT OF 2
f |  | 2 OUT OF 3
T |  | INDICATES A TIME DELAY BEFORE THE ACTION TAKES PLACE | [13 empty] | LOGIC DIAGRAM
¤ |  | INDICATES THAT EXECUTION IS INHIBITED UNTIL ASSOCIATED
SHUTDOWN VALVES ARE CONFIRMED CLOSED
R |  | RESET ACTION | [13 empty] | SIL
CAUSE
SYSTEM AREA |  |  | INITIATING EVENT (DESCRIPTION) |  | INSTRUMENT TAG NUMBER |  | INSTRUMENT LOCATION |  | LOGIC DIAGRAM | P&ID | SIL | SOR's | NOTES |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 |  | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
PCS |  |  | Masurare temperatura |  | 40-TT-007 |  | 50-PC-012-ACQ3A-CI |  |  | 13/18 | [5 empty] | A | bar: 16 to 39
PCS |  |  | Masurare debit |  | 40-FT-001 |  | 50-PC-012-ACQ3A-CI |  |  | 13/18 | [5 empty] | B |  |  |  |  | X | bar: 16 to 39
PCS |  |  | Indicator debit |  | 40-FS-001 |  | 50-AV-007-ACQ3A-VP |  |  | 13/18 | [5 empty] | C | [5 empty] | X | bar: 16 to 39
PCS |  |  | Masurare presiune diferentiala |  | 401-PDT- 001 |  | 401-V-001 |  |  | 12/18 | [5 empty] | D | [6 empty] | X | bar: 16 to 39
PCS |  |  | Indicator presiune |  | 40-PS-004 |  | 50-PC-001-ACQ3A-ET |  |  | 12/18 | [5 empty] | E | [7 empty] | X | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 300-TT-001 |  | 150-PC-003-ACQ3A-HC |  |  | 7/18 | [5 empty] | F | [8 empty] | X | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 302-TT-001 |  | 50-PC-004-ACQ3A-CI |  |  | 7/18 | [5 empty] | G | [9 empty] | X | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 30-TT-003 |  | 309-R-001 |  |  | 9/18 | [5 empty] | H | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 30-TT-004 |  | 309-R-001 |  |  | 9/18 | [5 empty] | I | bar: 16 to 39
PCS |  |  | Masurare presiune- Alarma |  | 300-PT-001 |  | 50-PC-003-ACQ3A-HC |  |  | 7/18 | [5 empty] | J | [10 empty] | X | bar: 16 to 39
PCS |  |  | Masurare presiune- Alarma |  | 302-PT-001 |  | 50-PC-004-ACQ3A-HC |  |  | 7/18 | [5 empty] | K | [11 empty] | X | bar: 16 to 39
PCS |  |  | Masurare presiune diferentiala/Alarma |  | 309-PDT- 001 |  | 309-R-001 |  |  | 9/18 | [5 empty] | L | [12 empty] | X | bar: 16 to 39
PCS |  |  | Masurare presiune diferentiala/Alarma |  | 309-PDT- 002 |  | 309-R-001 |  |  | 9/18 | [5 empty] | M | [13 empty] | X | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 30-TT-002 |  | 150-PC-001-ACQ3A-HC |  |  | 7/18 | [5 empty] | N | [14 empty] | X | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 30-TT-001 |  | 150-PC-002-ACQ3A-HC |  |  | 7/18 | [5 empty] | O |  | X | X | X | [11 empty] | X | X | bar: 16 to 39
PCS |  |  | Masurare debit |  | 30-FT-001 |  | 150-N-002-ACQ3A-HC |  |  | 7/18 | [5 empty] | P |  | X | X | X | bar: 16 to 39
PCS |  |  | Masurare presiune |  | 30-PT-001 |  | 150-GN-002-ACQ3A-HC |  |  | 7/18 | [5 empty] | Q | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 301-TT-002 |  | 301-V-001 |  |  | 7/18 | [5 empty] | R | bar: 16 to 39
PCS |  |  | Indicator nivel/Alarma |  | 301-LSHH-002 |  | 301-V-001 |  |  | 7/18 | [5 empty] | S | bar: 16 to 39
PCS |  |  | Indicator nivel |  | 301-LSH-001 |  | 301-V-001 |  |  | 7/18 | [5 empty] | T | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-ZIO-002 |  | 30-SDV-002 |  |  | 7/18 | [5 empty] | U | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-ZIC-002 |  | 30-SDV-002 |  |  | 7/18 | [5 empty] | V | bar: 16 to 39
PCS |  |  | Indicator nivel |  | 301-LSLL-001 |  | 301-V-001 |  |  | 7/18 | [5 empty] | W | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-ZIO-001 |  | 30-SDV-001 |  |  | 7/18 | [5 empty] | X | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-ZIC-001 |  | 30-SDV-001 |  |  | 7/18 | [5 empty] | Y | bar: 16 to 39
PCS |  |  | Indicator nivel/Alarma |  | 301-LSHH-001 |  | 301-V-001 |  |  | 7/18 | [5 empty] | Z | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-HS-001 |  | 30-SDV-001 |  |  | 7/18 | [5 empty] | AA | bar: 16 to 39
PCS |  |  | Indicator pozitie |  | 30-HS-002 |  | 30-SDV-002 |  |  | 7/18 | [5 empty] | AB | bar: 16 to 39
PCS |  |  | Masurare nivel |  | 301-LT-001 |  | 301-V-001 |  |  | 7/18 | [5 empty] | AC | bar: 16 to 39
PCS |  |  | Masurare nivel |  | 305-LT-001 |  | 305-V-001 |  |  | 8/18 | [5 empty] | AD | bar: 16 to 39
PCS |  |  | Indicator nivel |  | 305-LSLL-001 |  | 305-V-001 |  |  | 8/18 | [5 empty] | AE | bar: 16 to 39
PCS |  |  | Indicator nivel |  | 305-LSHH-001 |  | 305-V-001 |  |  | 8/18 | [5 empty] | AF | bar: 16 to 39
PCS |  |  | Masurare presiune |  | 30-PT-002 |  | 305-V-001 |  |  | 8/18 | [5 empty] | AG | bar: 16 to 39
PCS |  |  | Masurare presiune diferentiala/Alarma |  | 307-PDT- 001 |  | 307-F001 |  |  | 8/18 | [5 empty] | AH | bar: 16 to 39
PCS |  |  | Masurare presiune diferentiala/Alarma |  | 308-PDT- 001 |  | 307-F001 |  |  | 8/18 | [5 empty] | AI | bar: 16 to 39
PCS |  |  | Masurare presiune |  | 309-PT-001 |  | 309-R-001 |  |  | 9/18 | [5 empty] | AJ | bar: 16 to 39
PCS |  |  | Masurare temperatura |  | 309-TT-001 |  | 309-R-001 |  |  | 9/18 | [5 empty] | AK | bar: 16 to 40
PCS |  |  | Masurare temperatura/Alarma |  | 309-TT-002 |  | 309-R-001 |  |  | 9/18 | [5 empty] | AL | bar: 16 to 41
PCS |  |  | Masurare presiune /Alarma |  | 30-PT-003 |  | 50-PC-037-ACL3A-HC |  |  | 9/18 | [5 empty] | AM | bar: 16 to 43
PCS |  |  | Masurare debit |  | 30-FT-003/30-FIC-003 |  | 50-PC-033-ACL3A-HC |  |  | 9/18 | [5 empty] | AN | bar: 16 to 44
PCS |  |  | Masurare debit |  | 30-FT-002/30-FIC-002 |  | 50-PC-037-ACL3A-HC |  |  | 9/18 | [5 empty] | AO | bar: 16 to 45
PCS |  |  | Masurare presiune |  | 30-PT-005 |  | 50-PC-032-ACQ3A-HC |  |  | 9/18 | [5 empty] | AP | bar: 16 to 47
PCS |  |  | Masurare presiune/Alarma |  | 30-PT-004 |  | 50-PC-035-ACL3A-HC |  |  | 9/18 | [5 empty] | AQ | bar: 16 to 40; 42 to 49
PCS |  |  | Indicator nivel/Alarma |  | 309-LSLL-001 |  | 309-R-001 |  |  | 9/18 | [5 empty] | AR | bar: 16 to 44; 46 to 50
PROJECT NAME: FACILITATI DE SUPRAFATA PENTRU EXPLOATAREA DE GAZE P1 PODURI
PROJECT NUMBER: 856/2012
[22 empty] | 2 |  | 05.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [5 empty] | 33: NAN J.; 41: TRUSU M.
PROJECT PHASE: DE | [13 empty] | SHEET | [7 empty] | 1 |  | 2.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [5 empty] | 33: NAN J.; 41: TRUSU M.
[22 empty] | 0 |  | 01.01.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [5 empty] | 33: NAN J.; 41: TRUSU M.
DOCUMENT NUMBER: PR856-IN019-1_C&E DIAGRAM | [13 empty] | 6 | OF |  | 7 |  |  |  |  | REV |  | DATE |  |  |  | DESCRIPTION | [5 empty] | 25: PREPARED; 33: CHECKED; 41: APPROVED
ORIGINATOR

## C&E Diagram 7 (hidden)
|  |  |  | S.C STRATUM ENERGY ROMANIA LLC WILMINGTON SUCURSALA BLEJOI |  | CAUSE AND EFFECT DIAGRAM | [8 empty] | EFFECT | P&ID |  | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 9/18 | 12/18
S.C. TEAM OIL S.R.L.
PLOIESTI
LEGEND: | [7 empty] | NOTES: | [7 empty] | PERFORMED ACTION |  | ALARMA H=1000mm | ALARMA L=200mm | L≠0nmc/d | ALARMA H=900mm | ALARMA L=300mm | ALARMA H=35mc/h | L≠0nmc/d | PSD
SOR = Start-Up Override
X |  | SAFEGUARDING ACTION
' |  | INDICATES INPUTS WHICH MUST ALL BE PRESENT
|  | SIMULTANEOUSLY FOR AN OUTPUT SIGNAL TO BE GENERATED | [13 empty] | TAG NUMBER |  | 310-LAH-001 | 310-LAL-001 | 30-FAHH-001 | 310-LAH-001 | 310-LALL-001 | 30-FAH-001 | 30-FAHH-002 | D13
Ø |  | 1 OUT OF 2
f |  | 2 OUT OF 3
T |  | INDICATES A TIME DELAY BEFORE THE ACTION TAKES PLACE | [13 empty] | LOGIC DIAGRAM
¤ |  | INDICATES THAT EXECUTION IS INHIBITED UNTIL ASSOCIATED
SHUTDOWN VALVES ARE CONFIRMED CLOSED
R |  | RESET ACTION | [13 empty] | SIL
CAUSE
SYSTEM AREA |  |  | INITIATING EVENT (DESCRIPTION) |  | INSTRUMENT TAG NUMBER |  | INSTRUMENT LOCATION |  | LOGIC DIAGRAM | P&ID | SIL | SOR's | NOTES |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 30
PCS |  |  | Masurare nivel |  | 310-LT-001 |  | 310-R-001 |  |  | 9/18 | [5 empty] | B | bar: 1 to 8
PCS |  |  | Indicator debit |  | 30-FS-001 |  | 310-R-001 |  |  | 9/18 | [5 empty] | C | bar: 1 to 8
PCS |  |  | Masurare nivel |  | 310-LSH-001 |  | 310-R-001 |  |  | 9/18 | [5 empty] | D | bar: 1 to 8
PCS |  |  | Masurare nivel |  | 310-LSLL-001 |  | 310-R-001 |  |  | 9/18 | [5 empty] | E | bar: 1 to 8
PCS |  |  | Masurare debit |  | 30-FT-005 |  | 310-R-001 |  |  | 9/18 | [5 empty] | F | bar: 1 to 8
PCS |  |  | Indicator debit |  | 30-FS-002 |  | 310-R-001 |  |  | 9/18 | [5 empty] | G | bar: 1 to 8
PCS |  |  | PSD |  | D13 |  | 40-E-001 |  |  | 9/18 | [5 empty] | H | bar: 1 to 8
I
J
K
L
M
N
O
P
Q
R
S
T
U
V
W
X
Y
Z
AA
AB
AC
AD
AE
AF
AG
AH
AI
AJ
AK
PROJECT NAME: FACILITATI DE SUPRAFATA PENTRU EXPLOATAREA DE GAZE P1 PODURI
PROJECT NUMBER: 856/2012
[19 empty] | 2 |  | 05.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [13 empty] | Popa A. | [7 empty] | NAN J. | Trusu M.
PROJECT PHASE: DE | [13 empty] | SHEET |  |  |  | 2: 1; 4: 2.2014; 8: EMIS PENTRU CONSTRUIRE; 22: Popa A.; 30: NAN J.; 30: Trusu M.
[19 empty] | 0 |  | 01.01.2014 |  |  |  | EMIS PENTRU CONSTRUIRE | [13 empty] | Popa A. | [7 empty] | NAN J. | Trusu M.
DOCUMENT NUMBER: PR856-IN019-1_C&E DIAGRAM | [13 empty] | 7 | OF |  | 7 | 2: REV; 4: DATE; 8: DESCRIPTION; 22: PREPARED; 30: CHECKED; 30: APPROVED