## COVER
FOAIE DE DATE - REZERVOR COLECTARE SCURGERI INGROPAT
|  |  | LOCATION: |  |  |  | STATIE POMPARE TITEI SLOBOZIA
|  |  |  | EQUIPMENT NUMBER: | TK-001
|  |  |  | EQUIPMENT SERVICE: | REZERVOR INGROPAT
SERIAL NUMBER:
REQ / SPEC NO. :
PURCH ORDER NO. :
01 | 04.2022 | Emis pentru construire |  |  |  | Dan M. |  | Nan J.C. |  | Stan C. | Nan J.C.
00 | 06.2021 | Emis pentru comentarii |  |  |  | Dan M. |  | Nan J.C. |  | Stan C. | Nan J.C.
Rev.No. Rev.Nr. | Date Data | Description Descriere |  |  |  | Prepared Intocmit |  | Checked Verificat |  | PM Sef Proiect | Approved Aprobat
|  | FOAIE DE DATE - REZERVOR COLECTARE SCURGERI INGROPAT | [8 empty] | Faza: Detail
|  | Doc. No.: Doc.nr.: | PR1193-ME26-01 | [7 empty] | Rev.: 01
|  | Project Title: Titlul proiectului: | [6 empty] | Project no.: Proiect nr.: |  | Pag.Nr.:
|  | MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA | [6 empty] | 1193/2019 |  | 1 of 6

## Rev
MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA |  |  | Client Doc. No.: | PR1193-ME26-01
FOAIE DE DATE - REZERVOR COLECTARE SCURGERI INGROPAT |  |  | Rev. no. : | 01
|  |  | Page no. : | 2 of 6
| Revision No. Revizia Nr. | Description Descriere |  |  | Date Data
| 00 | Emis pentru comentarii |  |  | 06.2021
| 01 | Emis pentru construire |  |  | 04.2022

## 3
[14 empty] | FOAIE DATE MECANICA | [17 empty] | PR1193-ME26-01 | [7 empty] | Rev.: 00
[14 empty] | REZERVOR INGROPAT | [17 empty] | SHEET PAG.: |  |  | 3 OF 6
[32 empty] | BY |  |  | CHK'D |  |  |  |  | APPR.
[32 empty] | D.M. |  |  | N.J.C. |  |  |  |  | S.C.
PROJECT NO / PROIECT NR.: | [11 empty] | 1193/2019 | [19 empty] | REV | DATE |  |  |  | NAME |  |  | SIGNATURE
PROJECT TITLE / TITLU PROIECT: | [11 empty] | MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA | [19 empty] | 00 | 06.2021
MANUFACTURER/FABRICANT: | [31 empty] | 01 | 04.2022
1 | Item No. |  |  |  | TK-001 | [15 empty] | Number required |  |  |  | 1
2 | Equip. name |  |  |  | REZERVOR COLECTARE SCURGERI | [15 empty] | Fluidgroup |  |  |  |  | 1 |  |  | 2
3 | TON | [19 empty] | Category |  |  |  |  | I | II |  | III |  | IV
4 | Legal code | [19 empty] | Modul |  |  |  |  | G |  | H |  |  | H1
5 | Design Code |  |  |  | SR EN 12285-1 (Double shell) | [15 empty] | Location |  |  |  |  | outdoor (underground) | [8 empty] | indoor
6 | Manufacturer | [19 empty] | Orientation |  |  |  |  | horizontal | [5 empty] | vertical
7 | Requisition No. | [19 empty] | Special service |  |  |  |  | no |  | CO2 |  |  | H2S
8 | P & I -Diagram No. | [24 empty] | sour gas service | [7 empty] | class 1 |  |  |  |  | class 2
9 | OPERATING DATA
10 | Medium | [23 empty] | Apa sarata+titei
11 | Service description :
12 | - corrosion / erosion by
13 | - CO2 [vol-%] | [34 empty] | / |  |  | /
14 | - partial pressure |  |  |  |  | CO2 | [11 empty] | [bara] | [18 empty] | /
15
16 | Total / Max. operating volume | [16 empty] | [m³] |  |  |  | / | 13 |  | 5 |  |  | / | 13 | 4.25 | [6 empty] | /
17 | Operating temperature | [5 empty] | min. |  | / | norm. |  |  | / | max. |  |  |  | [°C] |  |  | / |  |  | / | 2 |  | / | 25 |  | / | 55 |  |  |  |  | / |  |  | /
18 | Operating pressure | [5 empty] | min. |  | / | norm. |  |  | / | max. |  |  |  | [barg] |  |  | / |  |  | / | 1 |  | / | 1.02 |  | / | 1.5 |  |  |  |  | / |  |  | /
19
20 | Liquid :
21 | - flow | [16 empty] | [m3/h]
22 | - density, at 20C | [16 empty] | [kg/m³] | [6 empty] | 800-1120
23 | - density at normal operation conditions | [16 empty] | [kg/m³] | [6 empty] | 800-1120
24 | - viscosity at 20C / normal operation conditions | [16 empty] | [cP] |  |  |  | / | [14 empty] | /
25 | Vapor :
26 | - flow | [16 empty] | [kg/h] | [6 empty] | NA | [7 empty] | -
27 | - molecular weight | [16 empty] | [kg/kmol] | [6 empty] | NA | [7 empty] | -
28 | - density at normal operation conditions | [16 empty] | [kg/m³] | [6 empty] | NA | [7 empty] | -
29 | DESIGN DATA
30 | Chamber | [17 empty] | Vessel | [9 empty] | Heating coil, Jacket
31 | Design Case | [17 empty] | I |  |  |  | II |  | III |  |  |  | I |  |  |  | II |  |  |  |  | III
32 | [18 empty] | operation |  |  |  | steam out |  | standstill |  |  |  | operation |  |  |  | steam out |  |  |  |  | standstill
33 | Design temperature | [16 empty] | [°C] | -29 | / | 60 |  | n.a. |  | n.a. | [5 empty] | /
34 | Design pressure | [16 empty] | [barg] |  | / | ATM |  | n.a. |  | n.a. | [5 empty] | /
35 | MECHANICAL DATA | [19 empty] | DESIGN
36 | Test press. |  | hydrost. | [5 empty] | pneum. |  |  |  |  | [barg] | acc.to code | [5 empty] | Design code | [9 empty] | SR EN 12285-1
37 | Relief valve set pressure | [12 empty] | [barg] | 0.02 | [5 empty] | Min.design met. temp. (MDMT) | [8 empty] | [°C]
38 | [20 empty] | Joint efficiency | [8 empty] | [%] | according to Code
39 | Diameter of shell | [8 empty] | ID |  | [mm] |  |  | 1500
40 | Length between tangent lines | [10 empty] | [mm] |  |  | 3000 | [5 empty] | Pulsation load : | [10 empty] | yes |  |  |  |  | no
41 | Height of skirt / legs / saddle to TL/CL | [12 empty] | [mm] | n/a | [5 empty] | - number of cycles
42 | Cone angle / length | [7 empty] | [°] / [mm] | [5 empty] | n/a | [5 empty] | - fatigue analysis | [10 empty] | ASME |  |  |  |  | Techn. Spec.
43 | Type of head | [13 empty] | Flat Ends
44 | Corrosion allowance / cladding | [10 empty] | [mm] |  |  | 3 |  | / | n/a |  |  | Nozzle loads
45 | Wall thickness of shell (incl. c. a.) I & II | [12 empty] | [mm] | 6 / 4 | [5 empty] | - calculation acc. to | [9 empty] | W.R.C. |  |  |  | BS 5500 |  |  |  |  | EN 13445
46 | - head / cone (incl. c. a.) I & II | [12 empty] | [mm] | 8 / 6 |  | / | n/a |  |  | - min. nozzle loads acc. to | [10 empty] | Techn. Spec. | [5 empty] | mfr's. std.
47 | - skirt / legs (without c. a.) | [12 empty] | [mm] | n/a |  | / | n/a
48 | Diam. of sump / dom | [5 empty] | OD |  |  | ID |  |  |  | [mm] | n/a
49 | - corrosion allowance / cladding | [12 empty] | [mm] | n/a |  | / |  |  |  | Wind design | [10 empty] | yes |  |  |  |  | no
50 | - wall thickn. (incl. c.a.) shell / head | [12 empty] | [mm] | n/a |  | / | [14 empty] | DIN 1055 |  |  |  | EUROCODE 1&3
51 | SURFACE TREATMENT | [30 empty] | other
52 | Shoot blasting : | [19 empty] | Earthquake design | [10 empty] | yes |  |  |  |  | no
53 | - press. parts |  |  |  | internal | [9 empty] | external |  | : | SA 21/2 | [13 empty] | EUROCODE 8 & P100
54 | - skirt / legs |  |  |  | inside |  |  | : | SA 21/2 | [5 empty] | outside |  | : | SA 21/2 | [13 empty] | other
55 | Painting acc. to: | [9 empty] | Paint. spec. | [9 empty] | - ag
56 |  |  |  | - pressure parts | [7 empty] | external | [8 empty] | - Tc
57 |  |  |  | - skirt / legs | [7 empty] | inside |  |  |  | outside |  |  |  |  | - building category
58 | Special coating | [10 empty] | internal epoxi (3) | [8 empty] | - building ground factor
59 | - coating type | [9 empty] | (4)
60 | Pickling and passivating (SS) | [10 empty] | internal |  |  |  | external |  |  |  |  | Fully dressed design | [10 empty] | yes |  |  |  |  | no
61 |  | glass beads blast. |  |  |  |  | brushing |  |  |  |  | internal |  |  |  | external

## 4
[8 empty] | FOAIE DATE MECANICA | [13 empty] | PR1193-ME26-01 | [6 empty] | Rev.: 01
[8 empty] | REZERVOR INGROPAT | [13 empty] | SHEET PAG.: |  |  |  | 4 OF 6
[22 empty] | BY |  |  |  | CHK'D |  |  | APPR.
[22 empty] | D.M. |  |  |  | N.J.C. |  |  | S.C.
PROJECT NO / PROIECT NR.: | [5 empty] | 1193/2019 | [15 empty] | REV |  | DATE |  |  |  | NAME | SIGNATURE
PROJECT TITLE / TITLU PROIECT: | [5 empty] | MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA | [15 empty] | 00 |  | 06.2021
MANUFACTURER/FABRICANT: | [21 empty] | 01 |  | 04.2022
1 | Item No. | TK-001 | [13 empty] | Equipment name |  | REZERVOR COLECTARE SCURGERI
2 | MATERIAL SPECIFICATION
3 | Shell / cladding |  | S355JR | [6 empty] | / | n/a |  |  |  |  | Gaskets :
4 | Heads / cladding |  | S355JR | [6 empty] | / | n/a |  |  |  |  | - vessel flanges |  |  |  |  | SR EN 1514-1,flat,IBC,graphite
5 | Skirt / Legs / saddle |  | S355JR | [6 empty] | / | n/a |  |  |  |  | - blinded nozzles |  |  |  |  | SR EN 1514-1,flat,IBC,graphite
6 | [15 empty] | - internal flanges | [7 empty] | n/a
7 | Nozzle pipes / cladding |  | P275NL1 | [6 empty] | / | n/a
8 | Nozzle flanges / cladding |  | P285NH | [6 empty] | / | n/a |  |  |  |  | Internals
9 | Vessel flanges / cladding |  | n/a | [6 empty] | / | n/a |  |  |  |  | - heating coil |  |  |  |  | n/a
10 | Type of cladding |  | n/a | [12 empty] | - demister / trays |  |  |  |  | n/a
11 | [15 empty] | Nameplate / bracket |  |  |  |  | MFR.Std |  |  |  |  | / | MFR.Std
12 | Bolts / nuts: | [14 empty] | Earthing lug |  |  |  |  | MFR.Std
13 | - vessel flanges |  | 42CrMo4QT | [6 empty] | / | 42CrMo4QT
14 | - blinded nozzles |  | 42CrMo4QT | [6 empty] | / | 42CrMo4QT |  |  |  |  | Foundation bolts / nuts | [9 empty] | /
15 | - internals (SS) |  | n/a | [6 empty] | /
16 | HEAT TREATMENT | [14 empty] | ACCESSORIES
17 | Stress relieving required : | [14 empty] | Demister | see sheet | [6 empty] | yes |  |  | no
18 | - process requirement | [7 empty] | yes |  |  |  | no |  |  | Trays | see sheet | [6 empty] | yes |  |  | no
19 | - by code required | [7 empty] | yes |  |  |  | no |  |  | Baffle plate at nozzle | [7 empty] | yes |  |  | no
20 | - partial stress relieving required | [7 empty] | yes |  |  |  | no |  |  | Vortex breaker at nozzle | [7 empty] | yes |  |  | no
21 | [15 empty] | Level indicator | [6 empty] | yes no
22 | INSULATION AND HEATING | [14 empty] | Support for vessel | [7 empty] | yes |  |  | no
23 | Insulation required |  | yes |  |  |  | no |  |  | by others | [5 empty] | Foundation bolts | [7 empty] | yes |  |  |  | no
24 | -shell / head thickn. [mm] |  | / | [12 empty] | Foundation bolts number req. x size
25 | - insulation type |  |  | HC |  |  |  | CC |  |  |  | PP |  |  |  | Templates (2 sets) | [7 empty] | yes |  |  |  | no
26 | - insulation clips |  |  | yes |  |  |  | no | [7 empty] | Sliding plates | [7 empty] | yes |  |  |  | no
27 | [15 empty] | Fire proofing
28 | Vessel heating req. |  | yes |  |  |  | no |  |  | by others : | [5 empty] | - thickness | [5 empty] | [mm] | n/a
29 | - type of heating |  |  |  | electrical | [10 empty] | Name plate : | [7 empty] | yes |  |  |  | no
30 |  |  |  |  | heat transfer fluid | [10 empty] | - engraved by: vendor | [7 empty] | yes |  |  |  | no
31 | - construction type |  |  |  | coil outside | [6 empty] | coil inside |  |  |  | Earthing lugs | [7 empty] | yes |  |  |  | no
32 |  |  |  |  | jacket | [6 empty] | mfr.type |  |  |  | Trunnions / lifting lugs for erection | [7 empty] | yes |  |  |  | no
33 |  |  |  |  | halfpipe
34 | Electrical heater : | [14 empty] | Clips for platforms, ladders, piping |  |  | 02 |  |  |  |  | yes |  |  |  | no
35 | - voltage / frequency |  | [V]/[Hz] | [6 empty] | / | [5 empty] | - total weight to be delivered | [5 empty] | [kg]
36 | - power |  | [KW] | [12 empty] | Top davit | [7 empty] | yes |  |  |  | no
37 | [15 empty] | Spare gaskets | [5 empty] | [sets] | 1
38 | Heat transfer fluid : | [14 empty] | Spare bolts / nuts (min.1 of each) | [5 empty] | [%] | 10
39 | - medium | LP-steam |  |  | MP-steam | [6 empty] | hot oil
40 | Fluid group |  |  |  | 1 |  |  | 2 | [7 empty] | Gas blanketing req. for transportation: | [7 empty] | yes |  |  | no
41 | Category |  |  |  | I |  |  | II |  |  | III |  |  | IV |  | - blanketing gas | [7 empty] | yes |  |  | no
42 | Module |  |  |  | G |  |  | H |  |  | H1 |  |  |  |  | - blanketing pressure | [5 empty] | [bar ga]
43 | Operating data |  |  |  |  | [°C] | [5 empty] | / |  |  |  | - incl. bottle, press. gauge & connect. | [7 empty] | yes |  |  | no
44 | - operating temp. min. / max. |  |  |  |  | [°C] | [5 empty] | / |  |  |  | Desiccant bags | [7 empty] | yes |  |  | no
45 | - operat. press. min. / max. |  |  |  |  | [bara] | [5 empty] | /
46 | - hydrostatic test pressure |  |  |  |  | [barg] | n/a | [8 empty] | Special tools required | [7 empty] | yes |  |  | no
47 | Total surface required |  |  |  |  | [m2] | [9 empty] | Hydraulic bolt tensioning device for bolts > M 36 | [7 empty] | yes |  |  | no
48 | O. dia. of tube / wallthickness |  |  |  |  | [mm] | [5 empty] | /
49 | - total length of tube |  |  |  |  | [mm] | [9 empty] | Torque & forces to be indicated in drwg. | [7 empty] | yes |  |  | no
50 | INSPECTION | [14 empty] | Oil buckets | [7 empty] | yes |  |  | no
51 | Inspection class | [14 empty] | Weirs | [7 empty] | yes |  |  | no
52 | Inspection authority | [14 empty] | Egualizing pipe | [7 empty] | yes |  |  | no
53 | [15 empty] | Inlet distribuitor | [7 empty] | yes |  |  | no
54 | Fabrication supervision by |  | MFR | [12 empty] | Distribution baffle | [7 empty] | yes |  |  | no
55 | [15 empty] | CERTIFICATION & TESTING
56 | Final Inspection |  | SC Conpet SA | [12 empty] | Test certificates |  |  |  | acc. to Code | [5 empty] | Techn. Spec. |  |  |  | Yes
57 | WEIGHTS & SHIPPING INFORMATION
58 | Shipping weight |  | (1) |  |  | [kg] | appr. | [8 empty] | Radiography |  | (RT) |  | acc. to Code | [5 empty] | Techn. Spec.
59 | Internals |  |  |  |  | [kg] | appr. |  |  | n/a | [5 empty] | test |  |  |  | full |  | at least spot
60 | Operating weight |  |  |  |  | [kg] | appr. |  |  | (*) | [5 empty] | Ultra sonic test |  | (UT) |  | acc. to Code | [5 empty] | Techn. Spec.
61 | Hydrotest weight at site |  |  |  |  | [kg] | appr.
62 | [15 empty] | Impact test |  |  |  | acc. to Code | [5 empty] | Techn. Spec.
63 | Fully dressed |  | (2) |  |  | [kg] | appr. |  |  | (**)
64 | [15 empty] | Max. hardness of base material | [8 empty] | [HV]
65 | Max. shipping dim. | ( L x B x H ) |  |  |  | [m] | 3000 |  |  | x | 1500 |  |  | x | 2700 | Max. chloride content of test water | [8 empty] | [ppm]
66 | [15 empty] | Other tests

## 5
[12 empty] | FOAIE DATE MECANICA | [10 empty] | PR1193-ME26-01 |  |  |  |  | Rev.: 01
[12 empty] | REZERVOR INGROPAT | [10 empty] | SHEET PAG.: |  |  | 5 OF 6
[23 empty] | BY |  |  | CHK'D |  | APPR.
[23 empty] | D.M. |  |  | N.J.C. |  | S.C.
PROJECT NO / PROIECT NR.: | [9 empty] | 1193/2019 | [12 empty] | REV |  | DATE |  | NAME | SIGNATURE
PROJECT TITLE / TITLU PROIECT: | [9 empty] | MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA | [12 empty] | 00 |  | 06.2021
MANUFACTURER/FABRICANT: | [22 empty] | 01 |  | 04.2022
1 | Item No. |  |  |  |  | TK-001 | [10 empty] | Equipment name |  |  | REZERVOR COLECTARE SCURGERI
2 | BOLTING
3 | Nozzle flange | [5 empty] | ISO metric |  | Yes | [7 empty] | Vessel flange |  |  |  | ISO metric | Yes
4 | bolting | [5 empty] | inch (UNC/UN) |  |  |  | stud bolts |  |  | Yes |  |  | bolting |  |  |  | inch (UNC/UN) |  |  | stud bolts |  |  | Yes
5
6 | NOZZLE DATA LIST
7 | Code requirement for flange standard | [11 empty] | EN 1092 |  | ASME B16.5 (ANSI) |  |  |  |  | ASME B16.47 Series A | [5 empty] | OTHER
8 | MARK |  |  |  | NO. | NOZZLE |  | FLANGE |  |  | FLANGE |  |  | FLANGE
9 |  |  |  |  | REQ. | SIZE |  | RATING |  |  | FACING |  |  | TYPE |  | GASKET |  |  | DESCRIPTION | [6 empty] | REMARKS
10 | [5 empty] | [DN] |  | [PN] | [5 empty] | [WN/LWN]
11 | R1 |  |  |  | 1 | 200 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Input Connection Drain
12 | R2a |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Nitrogen Pressure Gauge Connection
13 | R2b |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Nitrogen Fill Connection
14 | R3 |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Safety Valve Connection
15 | R4 |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Vent Connection
16 | R5 |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Pump Level Switch Connection
17 | R6 |  |  |  | 1 | 100 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Truck Suction Connection
18 | R7 |  |  |  | 1 | [13 empty] | Pump Suction Connection
19 | R8 |  |  |  | 1 | 50 |  | 16 |  |  | RF |  |  | WN |  |  |  |  | Level Gauge Connection
20 | MH |  |  |  | 1 | 1000 |  | 16 | [10 empty] | Manhole
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41 | REMARKS
42 |  |  | Applicable. Vendor shall design / provide / supply accordingly.
43 |  |  | Data / information must be completed by the bidder | [14 empty] | NOTES:
44 |  |  | with the bid.
45 | Abbreviations : | [15 empty] | - Material certification will be acc. SR EN 10204 :
46 | HC |  |  | = | Heat Conservation | [12 empty] | - type 3.1 for all elements.
47 | CC |  |  | = | Cold Conservation
48 | PP |  |  | = | Personnel Protection | [11 empty] | -Tank will be double shell and will be provided with a pressure
49 | WN |  |  | = | Welding Neck | [12 empty] | monitoring system in the space between shells.
50 | LWN |  |  | = | Long Welding Neck
51 | c.a. |  |  | = | corrosion allowance | [11 empty] | - FOR THE DATA SHEET SEE DOCUMENT PR1193_ME32
52 | n/a |  |  |  | not applicable
53 | TBC |  |  | = | To be confirmed
54
55 | (1) |  | Without internals.
56 | (2) |  | Fully dressed means shipping weight plus weight of
57 |  |  | piping, insulation, platforms and ladders.
58 | (3) |  | Internal epoxy coating and fiber glass epoxy coating/lining
59 |  |  | have to be resistant to given design and operating conditions
60 |  |  | and shall have appropriate chemical resistance. Coating/lining
61 |  |  | material type have to be approved by TECH Center&Lab
62 |  |  | ETTL-M.
63 | (4) |  | The external insulation shall comply with the standard ISO
64 |  |  | 12944, corosivity category Im3, with durability range H (high)
65 |  |  | for 15-25 years.
66 |  | (*) |  |  | For 80% filling degree.
67 |  | (**) |  |  | Shall be specified by Manufacturer.

## 6
|  |  |  | FOAIE DATE MECANICA |  |  | PR1193-ME26-01 |  |  |  | Rev.: 01
|  |  |  | REZERVOR INGROPAT |  |  | SHEET PAG.: |  | 6 OF 6
[7 empty] | BY |  | CHK'D |  | APPR.
[7 empty] | D.M. |  | N.J.C. |  | S.C.
PROJECT NO / PROIECT NR.: |  |  | 1193/2019 |  |  |  | REV | DATE |  | NAME | SIGNATURE
PROJECT TITLE / TITLU PROIECT: |  |  | MODERNIZAREA STATIEI DE POMPARE A TITEIULUI SLOBOZIA JUD. PRAHOVA |  |  |  | 00 | 06.2021
MANUFACTURER/FABRICANT: | [6 empty] | 01 | 04.2022
1 | Item No. | TK-001 |  |  | Equipment name | REZERVOR COLECTARE SCURGERI
2 | TANK SKETCH
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66