## COVER
MODERNIZARE STAȚIE DE POMPARE A ȚIȚEIULUI SLOBOZIA, JUD. PRAHOVA |  |  | CONPET S.A. |  | TEAM OIL | Doc. nr. : | PR1193-EL005-01
[6 empty] | Rev. nr. : | 01
LISTA INCARCARI ELECTRICE | [5 empty] | Pag. nr. : | 1 din 3
LISTĂ INCĂRCĂRI ELECTRICE
01 | 05.2022 | Emis pentru construire |  | BENGESCU Ad. | BENGESCU An. |  | STAN C. | NAN J.C.
00 | 06.2021 | Emis pentru comentarii |  | BENGESCU Ad. | BENGESCU An. |  | STAN C. | NAN J.C.
Rev. nr. | Data | Descriere |  | Intocmit | Verificat |  | Sef proiect | Aprobat
CONPET S.A. |  | LISTA INCARCARI ELECTRICE
|  | Doc. nr.: PR1193-EL005-01 | [5 empty] | Rev.: 01
|  | Titlul proiectului : |  |  | Nr. proiect : |  |  | Nr. pag. :
|  | MODERNIZARE STAȚIE DE POMPARE A ȚIȚEIULUI SLOBOZIA, JUD. PRAHOVA |  |  | Pr. 1193 / 2019 |  |  | 1 ÷ 3
Nume fisier : PR1193-EL005-01_Lista incarcari electrice

## REVISIONS
MODERNIZARE STAȚIE DE POMPARE A ȚIȚEIULUI SLOBOZIA, JUD. PRAHOVA |  |  | CONPET S.A. | TEAM OIL | Doc. nr. : | PR1193-EL005-01
[5 empty] | Rev. nr. : | 01
LISTA INCARCARI ELECTRICE |  |  |  |  | Pag. nr. : | 2 din 3
| Revizia nr. | Motivul reviziei |  |  |  |  | Data
| 00 | Emis pentru comentarii |  |  |  |  | 06.2021
| 01 | Emis pentru construire |  |  |  |  | 05.2022
Nume fisier : PR1193-EL005-01_Lista incarcari electrice

## TE-003
MODERNIZARE STAȚIE DE POMPARE A ȚIȚEIULUI SLOBOZIA, JUD. PRAHOVA | [5 empty] | CONPET S.A. |  |  |  |  | TEAM OIL |  | Doc. nr. : | PR1193-EL005-01
[13 empty] | Rev. nr. : | 01
LISTA INCARCARI ELECTRICE | [12 empty] | Pag. nr. : | 3 din 3
LISTA INCARCARI ELECTRICE - DULAP ELECTRIC POMPE 0,5 kV SI CIRCUITE AUXILIARE 0,4/0,23 kV - TE-003
NR. CRT. | CONSUMATOR | STARE | PUTERE INSTALATA | PUTERE ABSORBITA | PUTERE ABSORBITA POMPA | PUTERE MOTOR POMPA | FACTOR INCARCARE | RANDAMENT MOTOR | TENSIUNE | FACTOR DE PUTERE |  | PUTERE CONSUMATORI
[12 empty] | Functionare continua |  |  | Functionare intermitenta |  |  | Rezerva
- | - | - | Pi | Pa | Pap | Pm | - | ɳ | U | cos φ | tan φ | P | Q | S | P | Q | S | P | Q | S
|  |  | kW | kW | kW | kW | - | - | V | - | - | kW | kVAr | kVA | kW | kVAr | kVA | kW | kVAr | kVA
1 | Pompa evacuare titei ( VSD ) P-001 | A | 37 | - | 20 | 37 | 0.54054 | 0.92 | 500 | 0.99 | 0.14249 | 20 | 2.8498 | 20.202 | - | - | - | - | - | -
2 | Pompa evacuare scurgeri lichid ( DOL ) P-002 | A | 5.5 | - | 5.5 | 5.5 | 1 | 0.865 | 500 | 0.8 | 0.75 | 5.5 | 4.125 | 6.875 | - | - | - | - | - | -
3 | Tablou electric container echipamente electrice TE-004 | A | 3 | 2.096 | - | - | - | - | 230 | 0.9 | 0.48432 | 2.096 | 1.0151 | 2.3289 | - | - | - | - | - | -
4 | Tablou electric container relocat | A | 3 | 2.5 | - | - | - | - | 230 | 0.9 | 0.48432 | 2.5 | 1.2108 | 2.7778 | - | - | - | - | - | -
5 | Insotitor electric pompa evacuare titei P-001 HT-001 | A | 0.345 | 0.216 | - | - | - | - | 230 | 0.99 | 0.14249 | 0.216 | 0.030778 | 0.21818 | - | - | - | - | - | -
6 | Insotitor electric conducta aspiratie pompa evacuare titei P-001 HT-002 | A | 0.874 | 0.587 | - | - | - | - | 230 | 0.99 | 0.14249 | 0.587 | 0.083643 | 0.59293 | - | - | - | - | - | -
7 | Insotitor electric conducta refulare pompa evacuare titei P-001 + conducta contorizare debit pompe HT-003 | A | 1.472 | 0.982 | - | - | - | - | 230 | 0.99 | 0.14249 | 0.982 | 0.13993 | 0.99192 | - | - | - | - | - | -
8 | Insotitor electric conducta vas scurgeri lichid V-001 HT-004 | A | 0.483 | 0.322 | - | - | - | - | 230 | 0.99 | 0.14249 | 0.322 | 0.045883 | 0.32525 | - | - | - | - | - | -
9 | Dulap automatizare pompa evacuare titei P-001 | A | 1.35 | 1 | - | - | - | - | 230 | 0.9 | 0.48432 | 1 | 0.48432 | 1.1111 | - | - | - | - | - | -
10 | Circuit redundant - Dulap automatizare pompa evacuare titei | R | 1.35 | - | - | - | - | - | 230 | 0.9 | 0.48432 | - | - | - | - | - | - | 1 | 0.48432 | 1.1111
11 | Circuit iluminat exterior ELS-001 | I | 0.48 | 0.48 | - | - | - | - | 230 | 0.9 | 0.48432 | - | - | - | 0.48 | 0.23247 | 0.53333 | - | - | -
12 | Circuit de rezerva | R | 5.5 | - | - | - | - | - | 400 | 0.9 | 0.48432 | - | - | - | - | - | - | 5.5 | 2.6638 | 6.1111
| TOTAL |  | 59.004 | 8.183 | - | - | - | - | 500 | - | - | 33.203 | 9.9853 | 35.4231 | 0.48 | 0.23247 | 0.53333 | 6.5 | 3.1481 | 7.2222
[7 empty] | Incarcare maxima TE-003 |  |  |  | Pa max ( kW ) |  | Qa max ( kVAr ) |  | Sa max ( kVA ) |  | Ia max ( A )
[11 empty] | 33.683 |  | 10.2178 |  | 35.9564 |  | 41.5189

## DIESEL ELECTROGEN GROUP (hidden)
TEREMIA OIL MOBILE UNIT | [11 empty] | Doc. no. : | PR21101A901879-EL-010-03
ELECTRICAL LOAD LIST / LISTA INCARCARI ELECTRICE | [11 empty] | Rev. no. : | 03
[12 empty] | Page no. : | 14 of 15
LOAD LIST - DIESEL ELECTROGEN GROUP 82-GD-001 LISTA INCARCARI ELECTRICE - GRUP ELECTROGEN DIESEL 82-GD-001
CRT.NO. / NR. CRT. | CONSUMER / CONSUMATOR | STATUS / STARE | INSTALLED POWER PUTERE INSTALATA | ABSORBED POWER PUTERE ABSORBITA | VOLTAGE / TENSIUNE | POWER FACTOR FACTOR DE PUTERE |  |  | CONSUMERS POWER ( ACTIVE / REACTIVE / APPARENT ) PUTERE CONSUMATORI ( ACTIVA / REACTIVA / APARENTA )
[9 empty] | Continuous operation Functionare continua |  |  | Intermittent operation Functionare intermitenta |  |  | Spare Rezerva
- | - | - | Pi | Pa | U | cos φ | φ | tan φ | P | Q | S | P | Q | S | P | Q | S
|  |  | kW | kW | V | - |  |  | kW | kVAr | kVA | kW | kVAr | kVA | kW | kVAr | kVA
1 | Electrical indirect heater ( M101 ) Incalzitor electric indirect ( M101 ) 20-EH-001-C | A | 20 | 20 | 400 | 0.99 | 8.1096 | 0.14249 | 20 | 2.8498 | 20.202 | - | - | - | - | - | -
2 | Heat-tracings electrical panel Tablou insotitori electrici 82-DB-004 | A | #REF! | #REF! | 400 | 0.9 | 25.8419 | 0.48432 | #REF! | #REF! | #REF! | - | - | - | - | - | -
3 | Instrumental air electrical panel Tablou electric aer instrumental 82-DB-005 | A | #REF! | #REF! | 400 | 0.9 | 25.8419 | 0.48432 | #REF! | #REF! | #REF! | - | - | - | - | - | -
4 | Battery charger for gas electrogen group 82-GG-001 / Redresor baterie grup electrogen pe gaz 82-GG-001 BC-GG-1 | I | 0.5 | 0.5 | 230 | 0.9 | 25.8419 | 0.48432 | - | - | - | 0.5 | 0.24216 | 0.55556 | - | - | -
5 | Battery charger for gas electrogen group 82-GG-002 / Redresor baterie grup electrogen pe gaz 82-GG-002 BC-GG-2 | I | 0.5 | 0.5 | 230 | 0.9 | 25.8419 | 0.48432 | - | - | - | 0.5 | 0.24216 | 0.55556 | - | - | -
6 | Electrical heating resistance for gas electrogen group 82-GG-001 Rezistenta electrica incalzire grup electrogen pe gaz 82-GG-001 HE-GG-1 | I | 2 | 2 | 230 | 0.99 | 8.1096 | 0.14249 | - | - | - | 2 | 0.28498 | 2.0202 | - | - | -
7 | Electrical heating resistance for gas electrogen group 82-GG-002 Rezistenta electrica incalzire grup electrogen pe gaz 82-GG-002 HE-GG-2 | I | 2 | 2 | 230 | 0.99 | 8.1096 | 0.14249 | - | - | - | 2 | 0.28498 | 2.0202 | - | - | -
8 | PCS redundancy circuit Circuit redundant PCS 87-PCS-001 | A | 0.1 | 0.1 | 230 | 0.9 | 25.8419 | 0.48432 | 0.1 | 0.048432 | 0.11111 | - | - | - | - | - | -
9 | UPS electrical panel Tablou electric UPS 82-DB-UPS-001 | A | #REF! | #REF! | 230 | 0.9 | 25.8419 | 0.48432 | #REF! | #REF! | #REF! | - | - | - | - | - | -
10 | ESD redundancy circuit Circuit redundant ESD 79-SIS-001 | A | 0.416 | 0.416 | 230 | 0.9 | 25.8419 | 0.48432 | 0.416 | 0.20148 | 0.46222 | - | - | - | - | - | -
11 | F&G redundancy circuit Circuit redundant F&G 70-FGS-001 | A | 0.416 | 0.416 | 230 | 0.9 | 25.8419 | 0.48432 | 0.416 | 0.20148 | 0.46222 | - | - | - | - | - | -
12 | Control circuit / Circuit de comanda | I | 0.2 | 0.2 | 230 | 0.9 | 25.8419 | 0.48432 | - | - | - | 0.2 | 0.096864 | 0.22222 | - | - | -
13 | Firefighting electrical panel Tablou electric PSI 82-DB-PSI | R | 40 | - | 400 | 0.9 | 25.8419 | 0.48432 | - | - | - | - | - | - | 40 | 19.3729 | 44.4444
| TOTAL |  | #REF! | #REF! | 400 | - | - | - | #REF! | #REF! | #REF! | 5.2 | 1.1512 | 5.3737 | 40 | 19.3729 | 44.4444
[6 empty] | Maximum load Incarcare maxima 82-GD-001 |  |  | U (kV) | Pa max (kW) |  | Qa max (kVAr) | Sa max (kVA) |  | Ia max (A)
[9 empty] | 0.4 | #REF! |  | #REF! | #REF! |  | #REF!

## GAS_DIESEL ELECTROGEN GROUP (hidden)
GAS / DIESEL ELECTROGEN GROUP SIZING - G.G. / G.D.
DIMENSIONARE GRUP ELECTROGEN PE GAZ / DIESEL - G.G. / G.D.
For the sizing of the gas electrogen group ( G.G. ) has been considered the most unfavorable case, namely :
Pentru dimensionarea grupului electrogen pe gaz ( G.G. ) s-a luat in considerare cazul cel mai defavorabil, si anume:
1. All active consumers has been considered to be in operation, less one of the 15 kW pumps (20-P-001 or 44-P-002).
S-a considerat ca sunt in functionare toti consumatorii activi, mai putin una din pompele de 15 kW ( 20-P-001 sau
44-P-002 ).
2. With all these consumers in service, the maximum apparent power consumed is :
Cu toti acesti consumatori in functionare, puterea aparenta maxima consumata este :
Sa1 = Sa max - Sp = 216,23 - 15,87 = 200,36 kVA
3. When the remaining pump starts, its motor absorbs at startup an apparent power Sp :
In momentul in care porneste pompa ramasa, motorul acesteia absoarbe la pornire o putere aparenta Sp :
Sp = √3 x U x Ip = √3 x U x ( 6 x Im ) = √3 x 0,4 x 180A = 124,7 kVA , where / unde :
Im = √3 x Pm / ( U x cos φ x ƞ ) = 15 / ( √3 x 0,4 x 0,9 x 0,8 ) = 30,07 kW
4. Consequently, the total apparent power absorbed when the last pump start will be :
In consecinta, puterea aparenta totala absorbita in momentul pornirii ultimei pompe va fi :
Sa2 = Sa1 + Sp = 200,36 + 124,7 = 325,06 kVA
5. When operating as the main power source in a 24 hours/day regime, gas electrogen groups manufacturers
recommend as their load to be a maximum of 70% of the generators nominal apparent power, at power factor
cos φ = 0,8.
In cazul functionarii ca sursa principala de putere in regim de 24 ore/zi, producatorii de grupuri electrogene pe gaz
recomanda ca incarcarea acestora sa fie de maxim 70% din puterea nominala aparenta a generatoarelor, la factor
de putere cos φ = 0,8.
6. Taking into account these things, was chosen a gas electrogen group with the rated upper apparent power
superior to that obtained from the calculations, namely Sa = 345 kVA.
Tinand cont de aceste lucruri, s-a ales grupul electrogen pe gas cu puterea aparenta nominala superioara celei
obtinute din calcule, si anume Sa = 345 kVA.
NOTE / NOTA :
Regarding Diesel electrogen group ( G.D. ), in case of operation as a reserve power source, manufacturers
recommend as their load to be a maximum of 80% of the generators nominal apparent power, at power factor
cos φ = 0,8.
In conclusion, was chosen a Diesel electrogen group with rated apparent power Sa = 88 kVA.
Referitor la grupul electrogen Diesel ( G.D. ), in cazul functionarii ca sursa de putere de rezerva, producatorii
recomanda ca incarcarea acestora sa fie de maxim 80% din puterea nominala aparenta a generatoarelor, la factor
de putere cos φ = 0,8.
In concluzie, s-a ales un grup electrogen Diesel cu puterea aparenta nominala Sa = 88 kVA.

## Cable Data (hidden)
Cable Technical Data taken from IEE Recommendations for Electrical and
Electronic Equipment of Mobile and Fixed Offshore Installation (2nd edition 92)
Table 12.3 - XLPE, EP rubber twin and multicore
Cond. size | Curr. capacity | Volt Drop/A/m
mm2 | A
2.5 | 21 | 16
4 | 29 | 10
6 | 36 | 6.7
10 | 50 | 4
16 | 67 | 2.3
25 | 89 | 1.5
35 | 105 | 1.1
50 | 135 | 0.89
70 | 170 | 0.64
95 | 205 | 0.5
120 | 240 | 0.44
150 | 270 | 0.38
185 | 305 | 0.34
240 | 365 | 0.31
300 | 415 | 0.29
To select cable size base on Current capacity
Current cap. | Cable size |  | Impedance | Cable size | Breaker size | Cable size | Current cap.
0 | 2.5 |  | 0.29 | 300 | 0.5 | 2.5 | 21
21 | 4 |  | 0.31 | 240 | 3 | 2.5 | 21
29 | 6 |  | 0.34 | 185 | 7 | 2.5 | 21
36 | 10 |  | 0.38 | 150 | 15 | 2.5 | 21
50 | 16 |  | 0.44 | 120 | 30 | 6 | 36
67 | 25 |  | 0.5 | 95 | 50 | 16 | 67
89 | 35 |  | 0.64 | 70 | 100 | 35 | 105
105 | 50 |  | 0.89 | 50 | 150 | 70 | 170
135 | 70 |  | 1.1 | 35 | 250 | 150 | 270
170 | 95 |  | 1.5 | 25 | 400 | 240 | 480
205 | 120 |  | 2.3 | 16
240 | 150 |  | 4 | 10
270 | 185 |  | 6.7 | 6
305 | 240 |  | 10 | 4
365 | 300 |  | 16 | 2.5
415 | Oversize
Prepared by Mike Lim

## Breaker_Size (hidden)
Breaker size is based on Westinghouse Series C HMCP,MCP type MCCB.
Breaker size bigger than 400A is based on Seltronic type MC MCC 400-800A MCCB
0.5 | 3
3 | 7
7 | 15
15 | 30
30 | 50
50 | 100
100 | 150
150 | 250
250 | 400
400 | 600
600 | 800
800 | Too big